## Sheet1
Each Panel (Meter Board) is a Slave Device; MODBUS Addresses: 0 - 255
Each Slave Device: data is addressed from 0 to 65535
Design for 255 circuits. Circuit Configuration uses Holding Registers (R/W) Measurements use Input Registers ® Each Register type has its own address space : 0 - 65535
Interpreting Register Values
Reading | Actual Value |  | Units
Active Energy | Register Value * CT Rating |  | Wh
Active Power | Register Value * CT Rating |  | mW
Reactive Power | Register Value * CT Rating |  | mvar
Apparent Power | Register Value * CT Rating |  | mVA
Power Factor | Register Value * 0.01
Displacement Power Factor | Register Value * 0.01
Phase Angle | Register Value |  | Degrees
RMS Currents, Neutral Currents, P.E.Currents | Register Value * CT Rating |  | mA
Frequency | Register Value * 0.1 |  | Hz
L-L Voltages, L-N Voltages | Register Value*10 |  | dV: Tenth of a V
Slave Device
Holding Registers (R/W) Used for Circuit Configuration
Address (HEX) | Offset | Description | Notes | Size (16 bit words) | Access Level
Addresses 0x0 - 0xf for configurable BCM2 parameters
10 |  | Panel/Power Meter Configuration
| 0 | Meter Class: 1: Power Meter 2: Panel |  | 1 | R
| 1 | Meter Board ID |  | 1 | R
| 2 | Number of Circuit Positions |  | 1 | R
| 3 | Panel Layout: 1: One Column 2: Two Columns |  | 1 | R
| 4 | Panel Numbering: Odd/Even 0: Sequential 1: Odd/Even |  | 1 | R
| 5 | Mains CT Rating: 0 indicates CT is disabled |  | 1 | R
| 6 | Neutral CT Rating: 0 indicates CT is disabled |  | 1 | R
| 7 | P.E. CT Rating: 0 indicates CT is disabled |  | 1 | R
| 8 | Panel Breaker Rating |  | 1 | R
| 9 | Meter Type: 1: single-phase 2: split-phase 3; 3-phase |  | 1 | R
20 |  | Circuit Position Phases |  |  | R
| 0 | Mains A | Always A | 1 | R
| 1 | Mains B | used only if Meter Type is split-phase or 3-phase | 1 | R
| 2 | Mains C | used only if Meter Type is split-phase or 3-phase | 1 | R
| 3 | Circuit Position 1 Phase: 1: A, 2: B, 3:C |  | 1 | R
| 4 | Circuit Position 2 Phase: 1: A, 2: B, 3:C |  | 1 | R
|  | ….. | …. | …. | R
| 3 + c-1 | Circuit Position c Phase: 1: A, 2: B, 3:C |  | 1 | R
|  | ….. | …. | …. | R
| 255 | Circuit Position 256 Phase: 1: A, 2: B, 3:C |  | 1 | R
120 |  | Circuit Position CT Numbers |  |  | R
| 0 | CT # connected to Mains A | Unused, always 0 |  | R
| 1 | CT # connected to Mains B | Unused, always 0 |  | R
| 2 | CT # connected to Mains C | Unused, always 0 |  | R
| 3 | CT # connected to Circuit Position 1 |  | 1 | R
| 4 | CT # connected to Circuit Position 2 |  | 1 | R
|  | ….. | …. | …. | R
| 3 + c-1 | CT # connected to Circuit Position c |  | 1 | R
|  | ….. | …. | …. | R
| 255 | CT # connected to Circuit Position 255 |  | 1 | R
220 |  | Circuit Breaker Ratings |  |  | R
| 0 | Panel Breaker rating |  | 1 | R
| 1 | Circuit 1 Breaker Rating |  | 1 | R
| …… | …… | ….. |  | R
| c | Circuit c Breaker Rating |  | 1 | R
| ….. | …. | …. |  | R
| 255 |  |  |  | R
320 |  | Circuit CT Ratings |  |  | R
| 0 | Mains CT rating: 0 indicates CT is disabled |  | 1 | R
| 1 | Neutral CT Rating: 0 indicates CT is disabled |  | 1 | R
| 2 | P.E. CT Rating: 0 indicates CT is disabled |  | 1 | R
| 3 | Circuit 1 CT Rating |  | 1 | R
| …… | …… | ….. |  | R
| 3 + c-1 | Circuit c CT Rating |  | 1 | R
| ….. | …. | …. |  | R
| 255 |  |  |  | R
420 |  | Circuit Types |  |  | R
| 0 | Mains Circuit Type: Depends on meter type as shown below. Meter Type Circuit Type 3-phase: 4(3-phase) split-phase: 3(1-phase L-L-N) single-phase: 1 (L-N) |  |  | R
| 1 | Circuit 1 Circuit Type: 0: None, 1: 1-phase L-N, 2: 1-phase L-L, 3: 1-phase L-L-N, 4: 3-phase |  | 1 | R
| …… | …… | ….. |  | R
| c | Circuit c Circuit Type: 0: None, 1: 1-phase L-N, 2: 1-phase L-L, 3: 1-phase L-L-N, 4: 3-phase |  | 1 | R
| ….. | …. | ….
| 255 |  |  | 1 | R
Recommended Procedure for Changing Thresholds 1) Disable all Thresholds 2) Set values of thresholds, assertion delays and hysteresis 3) Enable the thresholds
520 |  | Frequency: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 |  |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
620 |  | Upper Critical Thresholds
| 0 |  |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
720 |  | Upper Warning Thresholds
| 0 |  |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
820 |  | Lower Warning Thresholds
| 0 |  |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
920 |  | Lower Critical Thresholds
| 0 |  |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
A20 |  | Hysteresis
| 0 | Hysteresis |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
B20 |  | Assertion Delays
| 0 | Assertion Delays |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
C20 |  | LineToLine Voltage: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
D20 |  | Upper Critical Thresholds
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
E20 |  | Upper Warning Thresholds
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
F20 |  | Lower Warning Thresholds
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
1020 |  | Lower Critical Thresholds
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
1120 |  | Hysteresis
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
1220 |  | Assertion Delays
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
1320 |  | LineToNeutral Voltage: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 1 | c-n |  | 1 | R/W
R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
1420 |  | Upper Critical Thresholds
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 1 | c-n |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
1520 |  | Upper Warning Thresholds
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 1 | c-n |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
1620 |  | Lower Warning Thresholds
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 1 | c-n |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
1720 |  | Lower Critical Thresholds
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 1 | c-n |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
1820 |  | Hysteresis
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 2 | c-n |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
1920 |  | Assertion Delays
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 2 | c-n |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  |  | R/W
1A20 | Active Energy: Circuit Summary Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
| …… | …… |  |  | R/W
| c | Circuit c |  | 1 | R/W
| …… | …… |  |  | R/W
| 255 |  |  | 1 | R/W
1B20 |  | Upper Critical Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… |  |  | R/W
| 511 |  |  |  | R/W
1D20 |  | Upper Warning Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… |  |  | R/W
| 511 |  |  | 1 | R/W
1F20 |  | Lower Warning Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… |  |  | R/W
| 511 |  |  |  | R/W
2120 |  | Lower Critical Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… |  |  | R/W
| 511 |  |  | 2 | R/W
2320 |  | Hysteresis
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… |  |  | R/W
| 511 |  |  |  | R/W
2520 |  | Assertion Delays
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
| …… | …… |  |  | R/W
| c | Circuit c |  | 1 | R/W
| …… | …… |  |  | R/W
| 255 |  |  |  | R/W
2620 | Active Power: Circuit Summary Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
| …… | …… | ….. |  | R/W
| c | Circuit c |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
2720 |  | Upper Critical Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 511 |  |  |  | R/W
2920 |  | Upper Warning Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 511 |  |  | 2 | R/W
2B20 |  | Lower Warning Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 511 |  |  | 2 | R/W
2D20 |  | Lower Critical Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 511 |  |  | 2 | R/W
2F20 |  | Hysteresis
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… |  |  | R/W
| 511 |  |  | 2 | R/W
3120 |  | Assertion Delays
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
| …… | …… |  |  | R/W
| c | Circuit c |  | 1 | R/W
| …… | …… |  |  | R/W
| 255 |  |  | 1 | R/W
3220 | Reactive Power: Circuit Summary Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
| …… | …… | ….. |  | R/W
| c | Circuit c |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
3320 |  | Upper Critical Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 511 |  |  | 2 | R/W
3520 |  | Upper Warning Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 511 |  |  | 2 | R/W
3720 |  | Lower Warning Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 511 |  |  | 2 | R/W
3920 |  | Lower Critical Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… | ….. |  | R/W
| 511 |  |  | 2 | R/W
3B20 |  | Hysteresis
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
| …… | …… |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
| …… | …… |  |  | R/W
| 511 |  |  | 2 | R/W
3D20 |  | Assertion Delays
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
| …… | …… |  |  | R/W
| c | Circuit c |  | 1 | R/W
| …… | …… |  |  | R/W
| 255 |  |  |  | R/W
3E20 | Apparent Power: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
3F20 |  | Upper Critical Thresholds
| 0 | a |  | 2 | R/W
| 2 | b |  | 2 | R/W
| 4 | c |  | 2 | R/W
| 6 | Circuit Position 1 |  | 2 | R/W
| …… | …… | ….. | 2 | R/W
| 6+(c-1)*2 | Circuit Position c |  | 2 | R/W
| …… | …… | ….. | 2 | R/W
| 511 |  |  | 2 | R/W
4120 |  | Upper Warning Thresholds
| 0 | a |  | 2 | R/W
| 2 | b |  | 2 | R/W
| 4 | c |  | 2 | R/W
| 6 | Circuit Position 1 |  | 2 | R/W
| …… | …… | ….. | 2 | R/W
| 6+(c-1)*2 | Circuit Position c |  | 2 | R/W
| …… | …… | ….. | 2 | R/W
| 511 |  |  | 2 | R/W
4320 |  | Lower Warning Thresholds
| 0 | a |  | 2 | R/W
| 2 | b |  | 2 | R/W
| 4 | c |  | 2 | R/W
| 6 | Circuit Position 1 |  | 2 | R/W
| …… | …… | ….. | 2 | R/W
| 6+(c-1)*2 | Circuit Position c |  | 2 | R/W
| …… | …… | ….. | 2 | R/W
| 511 |  |  | 2 | R/W
4520 |  | Lower Critical Thresholds
| 0 | a |  | 2 | R/W
| 2 | b |  | 2 | R/W
| 4 | c |  | 2 | R/W
| 6 | Circuit Position 1 |  | 2 | R/W
| …… | …… | ….. | 2 | R/W
| 6+(c-1)*2 | Circuit Position c |  | 2 | R/W
| …… | …… | ….. | 2 | R/W
| 511 |  |  | 2 | R/W
4720 |  | Hysteresis
| 0 | a |  | 2 | R/W
| 2 | b |  | 2 | R/W
| 4 | c |  | 2 | R/W
| 6 | Circuit Position 1 |  | 2 | R/W
| …… | …… | ….. | 2 | R/W
| 6+(c-1)*2 | Circuit Position c |  | 2 | R/W
| …… | …… | ….. | 2 | R/W
| 511 |  |  | 2 | R/W
4920 |  | Assertion Delays
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
4A20 | Power Factor: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
4B20 |  | Upper Critical Thresholds
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
4C20 |  | Upper Warning Thresholds
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3 + (c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
4D20 |  | Lower Warning Thresholds |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+ (c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
4E20 |  | Lower Critical Thresholds |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
4F20 |  | Hysteresis |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3 + (c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5020 |  | Assertion Delays |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5120 | Displacement Power Factor: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5220 |  | Upper Critical Thresholds
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5320 |  | Upper Warning Thresholds
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3 + (c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5420 |  | Lower Warning Thresholds |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+ (c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5520 |  | Lower Critical Thresholds |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5620 |  | Hysteresis |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3 + (c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5720 |  | Assertion Delays |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5820 | Phase Angle Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5920 |  | Upper Critical Thresholds
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5A20 |  | Upper Warning Thresholds
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3 + (c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5B20 |  | Lower Warning Thresholds |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+ (c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5C20 |  | Lower Critical Thresholds |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5D20 |  | Hysteresis |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3 + (c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5E20 |  | Assertion Delays |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
5F20 | RMS Current: Circuit Summary Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
| …… | …… | ….. |  | R/W
| c | Circuit c |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
6020 |  | Upper Critical Thresholds
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| c | Circuit c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
6120 |  | Upper Warning Thresholds |  | 1
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| c | Circuit c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
6220 |  | Lower Warning Thresholds |  | 1
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| c | Circuit c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
6320 |  | Lower Critical Thresholds |  | 1
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| c | Circuit c |  | 1 | R/W
| …… | …… | ….. | 1 | R/W
| 255 |  |  | 1 | R/W
6420 |  | Hysteresis |  | 1
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
| …… | …… |  | 1 | R/W
| c | Circuit c |  | 1 | R/W
| …… | …… |  | 1 | R/W
| 255 |  |  | 1 | R/W
6520 |  | Assertion Delays
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
| …… | …… | ….. |  | R/W
| c | Circuit c |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  |  | R/W
6620 |  | Neutral Currents: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | Neutral Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
6720 |  | Upper Critical Thresholds
| 0 | Neutral Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
6820 |  | Upper Warning Thresholds
| 0 | Neutral Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
6920 |  | Lower Warning Thresholds
| 0 | Neutral Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
6A20 |  | Lower Critical Thresholds
| 0 | Neutral Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
6B20 |  | Hysteresis
| 0 | Neutral Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  |  | R/W
6C20 |  | Assertion Delays
| 0 | Neutral Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  |  | R/W
6D20 |  | P.E. Currents: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | P.E Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
6E20 |  | Upper Critical Thresholds
| 0 | P.E Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
6F20 |  | Upper Warning Thresholds
| 0 | P.E Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
7020 |  | Lower Warning Thresholds
| 0 | P.E Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
7120 |  | Lower Critical Thresholds
| 0 | P.E Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  | 1 | R/W
7220 |  | Hysteresis
| 0 | P.E Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  |  | R/W
7320 |  | Assertion Delays
| 0 | P.E Current |  | 1 | R/W
| …… | …… | ….. |  | R/W
| 255 |  |  |  | R/W
Input Registers (R) Used for Measurements
Address (HEX) | Offset | Description | Notes | Size (16 bit words)
0 |  | Addresses 0x0 - 0xf for BCM2 readings |  |  | R
Frequency
10 |  | Circuit Positions
| 0 | Frequency |  | 1 | R
| …… | …… | ….. |  | R
| 255 |  |  |  | R
110 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 63 | Lower Critical 16 |  | 1 | R
L-L Voltages
150 |  | Circuit Positions
| 0 | A L-L |  | 1 | R
| 1 | B L-L |  | 1 | R
| 2 | C L-L |  | 1 | R
| …… | …… | ….. |  | R
| 255 |  |  |  | R
250 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 63 | Lower Critical 16 |  | 1 | R
L-N Voltages
290 |  | Circuit Positions
| 0 | A L-N |  | 1 | R
| 1 | B L-N |  | 1 | R
| 2 | C L-N |  | 1 | R
| …… | …… | ….. |  | R
| 255 |  |  | 1 | R
390 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 63 | Lower Critical 16 |  | 1 | R
Active Energy
3D0 |  | Circuit Summary Readings
| 0 | Mains |  | 2 | R
| 2 | Circuit 1 |  | 2 | R
…… | …….. | ……. |  | 2 | R
| c*2 | Circuit c |  | 2 | R
…… | …….. | ……. |  | ……. | R
| 384 | Circuit 192 |  | 2 | R
| 511 |  |  | 2 | R
5D0 |  | Circuit Summary Events
| 0 | Upper Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 63 | Lower Critical 16 |  | 1 | R
610 |  | Circuit Position Readings
| 0 | Mains A |  | 2 | R
| 2 | Mains B |  | 2 | R
| 4 | Mains C |  | 2 | R
| 6 | Circuit Position 1 |  | 2 | R
| … | ………….. |  | 2 | R
| 6 + (c-1)* 2 | Circuit Position c |  | 2 | R
| …… | ……. |  | 2 | R
| 388 | Circuit Position 192 |  | 2 | R
| 511 | locations 390-511 for future expansion
810 |  | Circuit Position Events | NOT SUPPORTED
| 0 | Upper Critical 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 15 | Upper Critical 16 | NOT SUPPORTED | 1
| 16 | Upper Warning 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 31 | Upper Warning 16 | NOT SUPPORTED | 1
| 32 | Lower Warning 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 47 | Lower Warning 16 | NOT SUPPORTED | 1
| 48 | Lower Critical 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 63 | Lower Critical 16 | NOT SUPPORTED | 1
Active Power
850 |  | Circuit Summary Readings
| 0 | Mains |  | 2 | R
| 2 | Circuit 1 |  | 2 | R
…… | …….. | ……. |  | 2 | R
| c*2 | Circuit c |  | 2 | R
…… | …….. | ……. |  | ……. | R
| 384 | Circuit 192 |  | 2 | R
| 511 |  |  | 2 | R
A50 |  | Circuit Summary Events
| 0 | Upper Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 63 | Lower Critical 16 |  | 1 | R
1
A90 |  | Circuit Position Readings
| 0 | Mains A |  | 2 | R
| 2 | Mains B |  | 2 | R
| 4 | Mains C |  | 2 | R
| 6 | Circuit Position 1 |  | 2 | R
| … | ………….. |  | 2 | R
| 6 + (c-1)* 2 | Circuit Position c |  | 2 | R
| …… | ……. |  | 2 | R
| 388 | Circuit Position 192 |  | 2 | R
| 511 | locations 390-511 for future expansion |  |  | R
C90 |  | Circuit Position Events | NOT SUPPORTED
| 0 | Upper Critical 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 15 | Upper Critical 16 | NOT SUPPORTED | 1
| 16 | Upper Warning 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 31 | Upper Warning 16 | NOT SUPPORTED | 1
| 32 | Lower Warning 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 47 | Lower Warning 16 | NOT SUPPORTED | 1
| 48 | Lower Critical 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 63 | Lower Critical 16 | NOT SUPPORTED | 1
1
Reactive Power
CD0 |  | Circuit Summary Readings
| 0 | Mains |  | 2 | R
| 2 | Circuit 1 |  | 2 | R
…… | …….. | ……. |  | 2 | R
| c*2 | Circuit c |  | 2 | R
…… | …….. | ……. |  | ……. | R
| 384 | Circuit 192 |  | 2 | R
| 511 |  |  | 2 | R
ED0 |  | Circuit Summary Events
| 0 | Upper Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 63 | Lower Critical 16 |  | 1 | R
|  |  |  | 1 | R
F10 |  | Circuit Position Readings
| 0 | Mains A |  | 2 | R
| 2 | Mains B |  | 2 | R
| 4 | Mains C |  | 2 | R
| 6 | Circuit Position 1 |  | 2 | R
| … | ………….. |  | 2 | R
| 6 + (c-1)* 2 | Circuit Position c |  | 2 | R
| …… | ……. |  | 2 | R
| 388 | Circuit Position 192 |  | 2 | R
| 511 | locations 390-511 for future expansion |  |  | R
1110 |  | Circuit Position Events | NOT SUPPORTED
| 0 | Upper Critical 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 15 | Upper Critical 16 | NOT SUPPORTED | 1
| 16 | Upper Warning 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 31 | Upper Warning 16 | NOT SUPPORTED | 1
| 32 | Lower Warning 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 47 | Lower Warning 16 | NOT SUPPORTED | 1
| 48 | Lower Critical 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 63 | Lower Critical 16 | NOT SUPPORTED | 1
1
Apparent Power
1150 |  | Circuit Position Readings
| 0 | Mains A |  | 2 | R
| 2 | Mains B |  | 2 | R
| 4 | Mains C |  | 2 | R
| 6 | Circuit Position 1 |  | 2 | R
| … | ………….. |  | 2 | R
| 6 + (c-1)* 2 | Circuit Position c |  | 2 | R
| …… | ……. |  | 2 | R
| 388 | Circuit Position 192 |  | 2 | R
| 511 | locations 390-511 for future expansion |  |  | R
1350 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 63 | Lower Critical 16 |  | 1 | R
1
Power Factor
1390 |  | Circuit Position Readings
| 0 | Mains A |  | 1 | R
| 1 | Mains B |  | 1 | R
| 2 | Mains C |  | 1 | R
| 3 | Circuit Position 1 |  | 1 | R
| … | ………….. |  | 1 | R
| 3 + (c-1) | Circuit Position c |  | 1 | R
| …… | ……. |  | 1 | R
| 194 | Circuit Position 192 |  | 1 | R
| 255 | locations 390-511 for future expansion |  |  | R
1490 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 63 | Lower Critical 16 |  | 1 | R
1
Displacement Power Factor
14D0 |  | Circuit Position Readings
| 0 | Mains A |  | 1 | R
| 1 | Mains B |  | 1 | R
| 2 | Mains C |  | 1 | R
| 3 | Circuit Position 1 |  | 1 | R
| … | ………….. |  | 1 | R
| 3 + (c-1) | Circuit Position c |  | 1 | R
| …… | ……. |  | 1 | R
| 194 | Circuit Position 192 |  | 1 | R
| 255 | locations 390-511 for future expansion |  |  | R
15D0 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 63 | Lower Critical 16 |  | 1 | R
1
Phase Angle
1610 |  | Circuit Position Readings
| 0 | Mains A |  | 1 | R
| 1 | Mains B |  | 1 | R
| 2 | Mains C |  | 1 | R
| 3 | Circuit Position 1 |  | 1 | R
| … | ………….. |  | 1 | R
| 3 + (c-1) | Circuit Position c |  | 1 | R
| …… | ……. |  | 1 | R
| 194 | Circuit Position 192 |  | 1 | R
| 255 | locations 390-511 for future expansion |  |  | R
1710 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 63 | Lower Critical 16 |  | 1 | R
1
RMS Currents
1750 |  | Circuit Summary Readings
| 0 | Mains |  | 1 | R
| 1 | Circuit 1 |  | 1 | R
…… | …….. | ……. |  | 1 | R
| c | Circuit c |  | 1 | R
…… | …….. | ……. |  | ……. | R
| 192 | Circuit 192 |  | 1 | R
255
1850 |  | Circuit Summary Events
| 0 | Upper Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 63 | Lower Critical 16 |  | 1 | R
1
1890 |  | Circuit Position Readings
| 0 | Mains A |  | 1 | R
| 1 | Mains B |  | 1 | R
| 2 | Mains C |  | 1 | R
| 3 | Circuit Position 1 |  | 1 | R
| … | ………….. |  | 1 | R
| 3 + (c-1) | Circuit Position c |  | 1 | R
| …… | ……. |  | 1 | R
| 194 | Circuit Position 192 |  | 1 | R
| 255 | locations 390-511 for future expansion |  |  | R
1990 |  | Circuit Position Events | NOT SUPPORTED
| 0 | Upper Critical 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 15 | Upper Critical 16 | NOT SUPPORTED | 1
| 16 | Upper Warning 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 31 | Upper Warning 16 | NOT SUPPORTED | 1
| 32 | Lower Warning 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 47 | Lower Warning 16 | NOT SUPPORTED | 1
| 48 | Lower Critical 1 | NOT SUPPORTED | 1
| …… | …… | …..
| 63 | Lower Critical 16 | NOT SUPPORTED | 1
1
Neutral Currents
19D0 |  | Circuit Position Readings
| 0 | Neutral Current |  | 1 | R
| …… | …… | ….. |  | R
| 255 |  |  | 1 | R
1AD0 |  | Circuit Position Events |  |  | R
| 0 | Upper Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 63 | Lower Critical 16 |  | 1 | R
P.E. Currents
1B10 |  | Circuit Position Readings
| 0 | P.E. Current |  | 1 | R
| …… | …… | ….. |  | R
| 255 |  |  | 1 | R
1C10 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
| …… | …… | ….. |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
| …… | …… | ….. |  | R
| 63 | Lower Critical 16 |  | 1 | R